Common Code Violations Found Upon Inspection

- Please note each building is reviewed to all applicable codes. Some of the following items may or not apply to your building.

- The following items are an overview of common violations, they are not all of the items in the Code that the office inspects.

- A copy of the Connecticut Fire Safety Code is available in the Fire Marshal’s Office.

- Fire Extinguishers-

  - The annual inspection tag has been updated within the past year.

  - On the reverse side of the tag a grid is available for the monthly inspection. The monthly inspection should be completed by the occupant, contain the date and the initials of the person performing the inspection.

  - During the monthly fire extinguisher inspection- Make sure the gauge is within the green area and indicating it is charged. Inspect the hose to make sure it is attached and not cracked. Make sure the pull pin on the handle is in place and secured by the safety plastic.

  - Make sure that fire extinguishers weighing less than 40 lbs are mounted at least 4 inches above the finished floor and not more than 5 feet above the finished floor. Fire extinguishers 40 lbs and over shall not be installed more than 3½ feet above the floor.

- Electrical-

  - Check electrical panels to make sure each circuit is properly labeled. Blank spots should be labeled as “blank.” Spots with a spare circuit should be labeled as “spare.”

  - There should be no storage in front of, or beside, electrical panels.

  - Open spots should be covered with an approved cover (not tape).

  - There should be no trip resistant devices installed on any circuits.

  - Check all outlets, switches, and electrical boxes to make sure they are properly covered.

  - Exposed electrical wires shall either be removed, certified and tagged as “dead,” or placed into a junction box.

  - Extension cords may not be used as a substitute for permanent wiring. Extension cords may not be permanently mounted, run through walls, windows, or under floors. If located in a business any extension cord shall have a sign “To Be Unplugged Prior To Closing.”

  - Check the back of power strips for the word “temporary.” Any power strip with the word temporary on it needs to be removed and replaced with a U.L. listed power strip that does not have the word “temporary.”

  - Power strips shall only be plugged directly into a wall outlet. Extension cords may not be plugged into power strips.

- Emergency Signs and Lights-

  - Emergency lights and exit signs should be tested monthly for not less than 30 seconds. A record of this monthly test needs to be maintained.

  - An annual test of the emergency lights shall be preformed for not less than 90 minutes, and a record of this test shall be maintained.

  - The test records should describe any problems noticed during both the annual and monthly inspection.

  - Make sure the exit signs are hung properly. If needed, check the arrows to be sure they point toward the exit.

  - Emergency lights should be properly aimed so that the floor area is illuminated.

- Alarm Systems-

  - Check pull stations to make sure they are clearly visible, within five feet of the exit, and easily accessible.

  - Have the alarm company’s annual inspection record available, and fix any problems noted.

  - The alarm panel should never indicate “trouble.” If it is please call the alarm company immediately to fix the problem.

  - The audible alarm should be within proper decibel levels throughout the building.

- Smoke Detectors-

  - Single-station smoke alarms should be in working order and have new batteries.

  - Replace smoke detectors older than ten years of age.

- Sprinkler Systems-

  - If your sprinkler heads are in a drop ceiling, make sure they have their decorative trim ring, and the ring is flush with the ceiling.

  - If you cannot see the sprinkler heads in your drop ceiling make sure they all have their covers (melt aways).

  - If you’re unsure which sprinkler type you have please contact your sprinkler company for assistance.

  - Storage should be lower than 18 inches from the bottom of the sprinkler head.

  - There should be nothing hanging from any sprinkler system components.

  - Have the sprinkler company’s annual inspection record available, and fix any problems noted.

  - A sprinkler wrench and the proper amount of spare sprinkler heads should be available.

- Kitchen Hood Systems-

  - Hoods should be cleaned on schedule. To find out how often your hood system needs cleaning please contact the Fire Marshal’s Office.

  - When cleaned, the hood system needs to be cleaned from top to bottom to bare metal; there can be no grease within the system after cleaning. Please note: It may be a good idea to observe the cleaning company. We have found that some only clean the most visible areas instead of the entire system.

  - Have the cleaning company’s inspection record available, and fix any problems noted.

  - The cleaning company should affix their label to the hood with the date cleaned, and the date of the next scheduled cleaning.

  - If there is a suppression system, have its inspection record available, and have any noted problems fixed. The suppression system should be inspected annually.

  - Make sure the cooking line is underneath the hood, and nozzles are angled over the cooking appliances.

  - Any additions or changes to the cooking line shall be approved by the Fire Marshal’s Office.

  - If you cook with vegetable or animal fats/oils a class “K” fire extinguisher is also required in the kitchen.

- Exits-

  - There may be no storage in exiting paths of travel.

  - Exits may not be blocked, and exits may not have keyed locks from the inside.

  - Be sure doors open, close and latch with ease.

- Storage-

  - For Business, Multi-Family Residential, and Assembly occupancies, any combustible storage areas in the basement of the building shall be 1-hour fire rated, or you may choose to remove the storage.

NOTE: There are exceptions to this and different types of structures not previously listed that may or may not need this rating.

  - There shall be no storage of flammable liquids or gasses below the previously listed types of buildings.

  - There shall be no storage of flammable liquids or gasses inside any occupancy unless it is within a rated cabinet or room.

- Availability-

  - When the Fire Marshal’s Office arrives for inspection we request that you have someone meet us who has knowledge of the structure(s), along with the keys and or codes to access every area of the building.

If you have any questions or concerns prior to, or after, your inspection please feel free to contact the Fire Marshal’s Office for assistance. We are open 8:00am – 4:30pm Monday through Friday at 860-355-6099.